8VA Toroidal Power Transformer

1.Product characteristics:

  - General description:

This device is a power transformer for use in low voltage power supply applications. It shall include 220Volt 50hertz primary and dual 14.9Volt 0.67AC amp secondary. The device must meet all requirements outlined in this specification.

- Electrical specifications

2.1.Circuit diagram

1.Red  0V

2.Red  220V

0.67A

3.Black   14.9V

4.Black    0V

2.2.Electrical performance

2.2.1.Rated primary voltage:0-220Vac

2.2.2.Rated frequency:50Hz

2.2.3.Rated output capacity:8VA

2.2.4.Secondary voltage deviation and regulation:

| Secondary | Output no-load voltage |  | Rated current | Output load voltage |  | Actual voltage regulation |
| --- | --- | --- | --- | --- | --- | --- |
|  | Rated | Actual measurement |  | Rated | Actual measurement |  |
| S1:3-4 | 14.9Vac±5％ | 14.98Vac±5％ | AC 0.67A | 12Vac±5％ | 12.06Vac±5％ | 19％ |

2.2.5.No-load current

The no load current shall current not exceed 8mA when a test voltage of 220V/50Hz is applied across the 220Vac primary input terminal.

2.2.6. No-load loss

The no-load loss shall not exceed 0.33Watt when a test voltage of 220V/50hZ is applie across the 220Vac primary input terminal.

D

H

The Picture Of  Installation

The Picture Of Form